XYZ Fire Districts

Pumper Service Test Manual

## Conducting Pumper Service Tests

# Conditions to Meet Before Annual Service Testing

- Apparatus must receive approval from maintenance division to conduct service testing.

  - No critical service write-ups exist that would prohibit less that optimal performance.

- All suction intake screens must be replaced prior to conducting the service test.

- Apparatus must be equipped and loaded as it normally would during fire ground usage.

- Apparatus scheduled for testing should be considered out of service for the duration of the test and arrangements for coverage for that apparatus will be made prior to the test.

- Any other tests that may be conducted annually for the apparatus will not take place during the pump service test unless the test does not interfere with the service test.

# General Service Test Information / Safety Considerations

- Crews conducting test should wear appropriate protective equipment for the test according to the a/h/j

    - Hearing protection and gloves should be considered a minimum

    - Unless otherwise noted, all tests must be conducted with all emergency and service lights operating that would normally be used at an actual emergency

    - Wheels should be chocked according to manufacturers instructions

# Equipment Needed for Service Test

## Test gauges

### master discharge

### master intake

### Pitot tube

## Speed counter

## Solid tip nozzles, stands, securing devices

## Hose

## Forms (Pumper Service Testing Form)

- Stopwatch

# Engine Speed Check

## Used to determine if engine is still operating at the governed speed it was purchased under

## Procedure:

### Under no load, increase throttle to rated rpms.

### Check with tachometer, handheld tachometer or speed counter

- Compare to service plate on pump panel

# Vacuum Test

## Used to check the priming device, pump, and hard intake hose for air leaks

## Procedure:

### Completely drain the pump of water

### Inspect all gaskets of intake hose and cap

### Look for foreign objects in the intake hose

### Connect 20’ of hard intake hose – check records for diameter

### Cap free end of intake hose

### All intake valves open, tightly capped, discharge valves closed, caps open

### Connect vacuum gauge – assure correct port

### Check oil level of priming pump reservoir

### Run priming device until gauge shows 22” Hg

### Record difference between test gauge and intake gauge

### Shut off engine – listen for air leaks

### Should not lose more than 10” of vacuum within 5 min.

# Hard Intake Hose Check*  (Optional)

### Used to determine performance of intake hose

### Use same procedure as vacuum test

### Support hose in direct line from pumper intake

### Place flashlight inside hose

### Use lexan cover to male side – use gasket

### Check hose for bubbles

# Pumping Test – Required Information

### Test begins when pressure and speed are obtained. Record the following at the beginning and every five minutes

### Pump discharge pressure

### Nozzle pressure

### Engine tachometer

### RPM using counter

### Engine coolant temperature

### Oil pressure

- Auto trans fluid – optional

# Pumping Test

## Capacity Test Procedure

100% of pumps rated capacity at 150 psi for 20 minutes

## Used to determine overall condition of pump and engine

### Correct for NEP

#### Lift (ft.) + intake hose friction loss

#### --------------------------------------------  =   psi

#### 2.3

Procedure:

### Connect hoselines according to chart

### Secure water supply

### Obtain prime

### Gradually increase pump speed until NEP reaches 150 psi

### Two stage pumps should be in volume

### Check flows and gauges for appropriate settings

# Pressure Control Test

## Used to determine that pressure control devices operate in accordance with manufacturer’s specifications

## Procedure:

### While pumping capacity at 150 psi, set control device to maintain this discharge pressure

### Close each of the flowing valves – one at a time, in no less than 3 seconds, no more than 10 seconds.

### Observe the pump discharge gauge. It should not rise more than 30 psi when each of the valves are closed.

### Restore the pump back to capacity at 150 psi.

### Reduce NEP to 90 psi without altering any valves or nozzle settings

### Set pressure control device at 90 psi

### Once control device is set at 90 psi, close each valve in no less than 3 seconds, and no more than 10 seconds.

### Observe pump discharge gauge. It should not rise more than 30 psi when each of the valves are closed.

# Pumping Test

## 70% test

### 70% of pump’s rated capacity at 200 psi for 10 minutes.

## Procedure:

### Set up hoselines to desired flow

### Two stage pumps can be in pressure or volume

### Using same method of capacity test – increase pressure to 200 psi

### Begin time – record readings every 5 minutes

# Pumping Test

## 50% test

### 50% of pumps rated capacity at 250 psi for 10 minutes

## Procedure:

### Set up hoselines to desired flow

### Two stage pump in pressure mode

### Using same method as capacity test – increase pressure to 250 psi

### Begin time – record readings every 5 minutes

# Pressure Control Test

## Procedure:

### While pumping at 250 psi, set the pressure control device to maintain this pressure.

### Close each of the valves one at a time, in no less than 3 seconds and no more than 10 seconds.

### Observe pump discharge pressure. It should not rise more than 30 psi when each valve is closed.

# Gauge and Flowmeter Test

## Used to determine if discharge pressures are accurate

## Procedure:

## Cap all discharge ports – including preconnects

## Open each discharge valve slightly

## Increase throttle to 150 psi.

## Compare individual gauges with master discharge gauge.

## Any gauges with a psi pressure difference needs repair.

# Tank to Pump Flow Test

## Used to determine if the piping between the tank and the pump is sufficient to supply the minimum amount of water specified by NFPA 1901.

## Pumpers with capacity of 500 GPM or less must flow 250 GPM from booster tank

## Pumpers with capacity of 500 GPM or greater must flow 500 GPM from booster tank.

(Departments may have specified greater flow rates)

## Procedure:

### Make sure water tank is filled to overflowing

### Close tank fill line, bypass cooling line, and all intake valves

### Attach sufficient hoselines to flow the required discharge rate

### With the pump in gear, open the discharge to the hose(s) attached and begin flowing water

### Increase the throttle until the maximum consistent pressure is obtained on the discharge gauge.

### Close the discharge valve without changing the throttle setting, and refill the tank (usually through top fill opening. Bypass valve may be opened to prevent overheating

## Reopen the discharge valve, and check the flow through the nozzle using a pitot tube or flowmeter. Adjust the engine throttle if the pressure needs to be brought back to desired setting

## Compare the flow rate being measured to NFPA or manufacturer-designed rate.

## Flow rate should be continued until at least 80% of the capacity of the tank is discharged.

# Test Results

## At no time during the test should the pumping system or engine show signs of overheating, power loss, or any other mechanical problems.

## Pump test results below 90% of the original test and rating of the pump requires the pump to be rated at a lower classification or taken out of service.

## Compare test results with results of previous years to determine possible system failures

  - Report any problems to maintenance officer.  Forward test results to proper person(s)

XYZ Fire Districts

Annual Pumper Service Test Record

| Service Test Date | Apparatus No. | Serial Number | Manufacturer | Year Built | Pump GPM |
| --- | --- | --- | --- | --- | --- |
| Test Location | Tested By: |

Test 1 – Engine Speed Check:  Compare hand tachometer reading to engine service plate on pump panel    Pass _______  Fail________

Test 2 - Vacuum Test:________________________________________________________________________________________________

(20’ 6” hard suction capped for 5 minutes with less that 10mm hg drop

Test 3 – Pumping Test – Capacity Test:  10 Minutes at 100% of Rated Capacity at 150psi

Hose Layout Used:____________________________________________  Tip Size:_______________________________________

| TIME | Oil Pressure | Engine Temp. | Engine RPM | Pump Speed | Pump Pressure | Vacuum Pressure | Tip Size | Tip Pressure | Total GPM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Start |  |  |  |  |  |  |  |  |  |
| 10 Minutes |  |  |  |  |  |  |  |  |  |
| 15 Minutes |  |  |  |  |  |  |  |  |  |
| 20 Minutes |  |  |  |  |  |  |  |  |  |
| Spurt Test |  |  |  |  |  |  |  |  |  |

Test 4 – Pressure Control Test: (Pressure Control Device Type):________________________________

(Conduct before shutting down capacity test-shut valves, 30 psi increase maximum allowable)

Test 5 – Pumping Test - 10 Minutes at 70% of Rated Capacity at 200 PSI.

Hose Layout Used:_______________________________________________________________________________

| TIME | Oil Pressure | Engine Temp. | Engine RPM | Pump Speed | Pump Pressure | Vacuum Pressure | Tip Size | Tip Pressure | Total GPM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Start |  |  |  |  |  |  |  |  |  |
| 5 Minutes |  |  |  |  |  |  |  |  |  |
| 10 Minutes |  |  |  |  |  |  |  |  |  |

Test 6 – Pumping Test - 10 Minutes at 50% of Rated Capacity at 250 PSI.

Hose Layout Used:_______________________________________________________________________________

| TIME | Oil Pressure | Engine Temp. | Engine RPM | Pump Speed | Pump Pressure | Vacuum Pressure | Tip Size | Tip Pressure | Total GPM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Start |  |  |  |  |  |  |  |  |  |
| 5 Minutes |  |  |  |  |  |  |  |  |  |
| 10 Minutes |  |  |  |  |  |  |  |  |  |

Test 7 – Pressure Control Test – (Conduct at conclusion of 250 psi Pumping Test)

| Valve / Discharge (Lines used for test) | Discharge Pressure | Master Intake Pressure | Master Intake Pressure with Valve Closed | Pass / Fail (No more than 30 psi each) |
| --- | --- | --- | --- | --- |
| Discharge 1 |  |  |  |  |
| Discharge 2 |  |  |  |  |
| Discharge 3 |  |  |  |  |

Test 8 – Tank to Pump Flow Test:

| Pump Size In GPM’s | Flow Requirement | Line Arrangement for Flow Requirement | Flow tank to gpm requirement (Tip Size) | Pass / Fail (Meet flow rate requirement) |
| --- | --- | --- | --- | --- |
| 500 GPM or less | 250 gpm from booster tank | 1 – 3” line |  |  |
| 500 GPM or greater | 500 gpm from booster tank | 2 – 2 ½” lines |  |  |

Remarks_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

SOUTHWEST UNITED FIRE DISTRICTS

MAINTENANCE DIVISION

Vehicle Malfunction Report

Vehicle #________________________						Date:_____________________

Mileage:________________________	Engine Hours:___________________	Pump Hours:______________

Description of problem(s):

1.___________________________________________________________________________________________________________________________________________________________________________________________________

2.___________________________________________________________________________________________________________________________________________________________________________________________________

3.___________________________________________________________________________________________________________________________________________________________________________________________________

4.___________________________________________________________________________________________________________________________________________________________________________________________________

5.___________________________________________________________________________________________________________________________________________________________________________________________________

Circle:		In Service		Out of Service

Name:_________________________________			Signature:________________________________

Title:__________________________________

Officer:________________________________			Signature:________________________________

Rank:_________________________________